## Slide 1: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Agenda
Thimphu, Bhutan
18th to 20th July 2018

## Slide 2: Day-1 (18-July-2018)
Time | Description
1115-1300 | Session-I “Introduction to power system simulation using PSSE” Views in Power flow interface File types in PSSE Program settings PSSE Documentation Creating a new case Familiarization with data types / Adding and Modifying power flow data
1300-1400 | Lunch
1400-1530 | Session-II “Getting started in power flow with PSSE” Power flow solution Hands-on exercise in power flow
1530-1700 | Session-III “Diagrams in PSSE” Diagram view and Diagram Toolbar Diagram options Creating diagram of a subsystem Hands-on exercise

## Slide 3: Day-2 (19-July-2018)
Time | Description
1000-1200 | Session-I “Exploring power flow solution” Solution methods Solution parameters Viewing power flow results Limit checking reports Hands-on exercise: Examining power flow results
1200-1300 | Session-II “Toolbars and Diagrams” Usage of common toolbars Program preferences
1300-1400 | Lunch

## Slide 4: Day-2 (19-July-2018)…contd..
Time | Description
1400-1600 | Session-III “Introduction to Fault Analysis” Generator and Load conversion Setting up a sav case for fault analysis Balanced switching options ANSI and IEC fault analysis options Hands-on exercise on fault level calculation at network buses Charging studies
1600 - 1700 | Session- IV “Data checking in PSSE” Using program features for bad data detection Handling a blown-up power flow case Hands-on exercise

## Slide 5: Day-3 (20-July-2018)
Time | Description
1000-1200 | Session-I “Introduction to Dynamic simulation” Basic logic flow for dynamic simulation activities Setting up a *.dyr case for dynamic simulation Dynamics documentation Defining channels for simulation output Initializing a dynamics case
1200-1300 | Session-II “Dynamic simulation activities” Applying disturbance Hands-on exercise on running a basic dynamic simulation
1300-1400 | Lunch
1400-1530 | Session-III “Contingency analysis” Creating data files for basic contingency analysis Transfer limits calculation in PSSE (Activity TLTG) Contingency ranking in PSSE

## Slide 6: This page is intentionally kept blank

## Slide 7: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Session I : Introduction to power system simulation using PSS/E
Day-1
Thimphu, Bhutan
18th to 20th July 2018

## Slide 8
  Electric Power system => Largest machine every built
    Interaction amongst millions of devices and their controllers
    Simulate => Assess impact without disturbance / interruption
Power System Simulation
  Generation Delivery Consumption

## Slide 9
Simulation => Actual run of a model system to gain insight into its performance.
Steps in Simulation =>
Modelling is the Transition of a given Physical problem into it’s Mathematical representation
Introduction to Simulation…(1)
Simulation
Programming
Analysis
Modelling
Probability & Statistics
(Assumptions)

## Slide 10: Power System study : Timelines and Categories
Steady State
  Time ‘t’ is invariant => Frequency ‘f’ is invariant
  Power flow studies
Short-circuit
  Instant of switching (t=0+)
Transient Stability (Time-domain)
  Time ‘t’ is variant
  t = 0+ to tens of seconds
Small-signal stability (Frequency domain)
  Eigenvalue analysis
Electro-magnetic transient analysis (Fast transients)

## Slide 11
Time Regimes in power system simulations

## Slide 12
Per Unit (p.u.) System
In p.u. system, power system quantities (such as V, I, R, X, VA, P and Q) are expressed as decimal fractions of chosen base values.
p.u. values of circuit parameters are the same on either side a transformer.
Choosing base value:
Can choose any value as the Base Value
Choose value to make computation efficient
In PSSE, usually choose:
  MVAbase = 100.0
Change of Base:

## Slide 13
PSSE Program overview
Tool for Linear power system analysis
  Steady state power flow
  Short circuit studies
  Transient simulation (Linear differential equations)
Ancillary programs:
  PSSPLT
  Vcurve analysis
  Transmission line parameter estimation tool (Lineprop)
Functions like a sophisticated and powerful handheld calculator
PSS/E Program overview…(1)

## Slide 14
Program Overview…(2)
Source : PSSE 34.2 PAG-1

## Slide 15
Program overview…(3)
File Classes | Created by | Type | Accessible to | Formats
Working files | PSSE | Binary | PSSE | -
Data input files | User via Text Editor | Text | PSSE and user | *.raw, *.dyr
Output listing files | PSSE | Text | User | -
Channel output files | PSSE | Binary | PSSE | *.out, *.outx
Response files | User via Text Editor | Text | PSSE and user | *.idv
Saved case and Snapshot files | PSSE | Binary | PSSE | *.sav, *.snp
Source : PSSE 34.2 PAG-1

## Slide 16
Program overview…(4)

## Slide 17
Program overview…(5)
Spreadsheet View
Output Bar / Tree View
Command Line Status Bar
Toolbar
Diagram
View

## Slide 18
Program overview…(6)
PSSE Help Topics
PSSE Topicwise Help : Press F1

## Slide 19
PSSE Startup
Run => Siemens PTI => PSSE 34.x =>
Starts in EXAMPLE file directory (Default)

## Slide 20
Program Options…(1)

## Slide 21
Program Options…(2)

## Slide 22
Creating a new case
File => New =>

## Slide 23: Power Flow Modeling Data

## Slide 24
Network Data Tabs…Bus Data…(1)
Buses => Similar to Geographical Nodes in power system
Mandatory information : Bus number, Bus Name, ID (Type of Bus), Voltage Level (Base KV)

## Slide 25
Network Data Tabs…Bus Data…(2)
Bus Types:

## Slide 26
Network Data Tabs…Load Data
Mandatory information : Bus number, ID, Pload & Qload (or other types)
Types : Constant P, Constant I, Constant Z
Scalable / Non-scalable, Interruptible / Non-interruptible

## Slide 27
Network Data Tabs…Machine Data
Mandatory information : MVAbase, Pmax, Pmin, Qmax, Qmin, Pgen, Vscheduled, Xsource, Xtran
All Machines attached to a Plant (viz. a collective of machines)
For multiple machines => Use IDs to identify units
Importance of individual parameters
Generator transformer modelling => Implicit / explicit

## Slide 28
Network Data Tabs…Plant Data
Non-editable
Editable

## Slide 29
Network Data Tabs…Shunt Data
Switched Shunt
Fixed Shunt

## Slide 30
Network Data Tabs…AC Lines
Mandatory information : From Bus, To Bus, Branch-ID, R, X, B (in p.u.), Ratings, Length, Line Shunts (From end / To end)

## Slide 31
Network Data Tabs…2-winding transformer
Mandatory information : From Bus, To Bus, R, X, Ratings, Tap Settings

## Slide 32
Network Data Tabs…Area/ Owner / Zone
Areas
Owners
Zones

## Slide 33: This page is intentionally kept blank

## Slide 34: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Session II : Getting started with power flow in PSS/E
Day-1
Thimphu, Bhutan
18th to 20th July 2018

## Slide 35
Power flow solution options
Robust method : Newton-Raphson

## Slide 36
Power flow solution

## Slide 37
Modifying power flow data…(1)
Power flow data modification options:
  Change topology (Split buses, Join buses, Move network elements, etc.)
  Scale Load / Generation (Bus wise / Subsystem wise)
Topology Toolbar

## Slide 38
Modifying power flow data…Scale…(2)

## Slide 39
Modifying power flow data…Scale…(3)
Scale Load / Generation / Fixed Shunts
Scale Active / Reactive power components
Utility :
  Change subsystem wise data

## Slide 40
Exercise : Power flow modelling…(1)
Steam :
MVAb= 58 MVA Pmax = 50 MW Pmin = 20 MW
Pgen = 40 MW Qmax = 20 MVar Qmin = -10 Mvar
Xsource = 13%
Xtran = 14.5%
Vsched = 220
Hydro:
MVAb= 28 MVA Pmax = 23 MW Pmin = 0 MW
Pgen = 20 MW Qmax = 10 MVar Qmin = 0 Mvar
Xsource = 20%
Xtran = 12%
Vsched = 21.21
Active Power: 50 MW
Power factor : 0.9
Active Power: 50 MW
Reactive : 15 MVAR
220 kV
21 kV
33 kV
System Base : 50 Hz, 100 MVA
Swing bus (Type-3) : Bus3
FSC = ?
X = 12% (System base)
Rating = 40 MVA
X = 12% (System base)
Rating = 70 MVA

## Slide 41
Exercise : Power flow modelling…(2)
Line Data | Impedances (PU on System Base) R X B |  |  | (MVA) Rate A Rate B Rate C |  | 
Bus1 – Bus2 | 0.0003 | 0.0124 | 0.5435 | 132 | 200 | 220
Bus1 – Bus4 | 0.0002 | 0.0020 | 0.0068 | 132 | 200 | 220
Bus2 – Bus4 | 0.0001 | 0.0015 | 0.0049 | 132 | 200 | 220
Problem statement:
Model the standard 5 bus system above using data given
Use appropriate bus types (Refer previous slides on Bus-type)
Save as ‘Case-1.1.sav’
Solve power flow
Find the highest loaded line (in percentage terms)

## Slide 42: This page is intentionally kept blank

## Slide 43: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Session III : Diagrams in PSS/E
Day-1
Thimphu, Bhutan
18th to 20th July 2018

## Slide 44
Tree Views in PSSE
Tree views in PSSE present useful information at a glance
To enable tree views for a particular category => View > Tick/Untick
Useful for creating diagrams, plotting transient simulation results, viewing model data, etc.
Data
Items
In
Tree view

## Slide 45
Diagram View in PSSE
For ease of visualisation
SLD (Single Line Diagram) form
Add/modify network elements
Perform power flow solution
View results

## Slide 46
Single Line Diagram View (*.sld file)

## Slide 47: To Create a New Diagram

## Slide 48: Diagram Menu Options

## Slide 49: Diagram Properties...(1)
Menu Bar -> Diagram -> Properties
Diagram Annotation
Diagram Range Checking
Diagram Settings
Used to modify visualisation experience on SLD files

## Slide 50: Diagram Properties...(2)
Diagram Range Checking
Additional Diagram settings

## Slide 51: Diagram Preferences
Menu bar -> Edit -> Preferences
For ‘Grow’ activity
For control on bind/unbind mode

## Slide 52: Diagram Preferences
Menu bar -> Edit -> Preferences
For ‘Grow’ activity
For control on bind/unbind mode

## Slide 53
Exercise
Open Case 1_1.sav- Solve the system using Full Newton-Raphson Solution Method (under Powerflow > Solutions) with Defaults Options.
Create a one-line diagram of the Case 1_1.sav system. Refer to the attached one-line diagram to check your progress.
Use auto-draw to add the system components. When you are finished, save the diagram information to a file called Case 1-1.SLD
Automate power flows
Check branch loadings as percentage of RATE-B
Tap Branch between Bus-1 and Bus-2 (at Bus#606) with 40:60 ratio of impedances between Bus-1 to Bus-6 and Bus-6 to Bus-2. Add Load-SEC with P=5 MW, p.f. 0.9.
Save Modified case as Case 1_2.sav
Find Pair of buses with maximum angular difference

## Slide 54
Case 1_1.sld

## Slide 55
Case 1_1.sld => Branch Overload Checking

## Slide 56
Case 1_2tapped.sld => Network after tapping

## Slide 57: Thank You !!