## Slide 1: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Agenda
Day-3
Thimphu, Bhutan
18th to 20th July 2018

## Slide 2: Day-3 (20-July-2018)
Time | Description
0930-1130 | Session-I “Introduction to Dynamic simulation” Basic logic flow for dynamic simulation activities Setting up a *.dyr case for dynamic simulation Dynamics documentation Defining channels for simulation output Initializing a dynamics case
1130-1230 | Session-II “Dynamic simulation activities” Applying disturbance Hands-on exercise on running a basic dynamic simulation

## Slide 3: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Session I : Introduction to Dynamic Simulation
Day-3
Thimphu, Bhutan
18th to 20th July 2018

## Slide 4
Dynamic Simulation – Overview…(1)
Simulation of the power system response to disturbances.
Disturbances:
branches and bus faults with or without protection failure (stuck breaker)
opening of branches without fault
trip of generators with or without faults
trip of loads
Dynamic simulation requires the solution of nonlinear differential equations
PSS®E calculates the time response of the system by numerical integration of the system differential equations

## Slide 5
Dynamic Simulation – Overview…(2)
Differential equations are embedded in the models of the generators, excitation systems, etc. and are expressed in block diagram form
Models are linked through the power system network, which is represented by algebraic equations
Non-linearities such as limits and saturation can be addressed accurately using detailed models

## Slide 6
Dynamic Simulation – Network Solution
Network represented by a nodal admittance matrix (Y-bus)
Unlike in EMTP, network dynamics are not represented in stability programs. Network represented using positive sequence quantities
Numerical Integration Method :
-Uses Modified Euler method
-PSS/E integration method requires the integration step to be smaller than the smallest time constant
Programs like TSAT (DSA Tools) use Runge Kutta Method of integration (Faster, More robust)

## Slide 7
Dynamic Simulation – P-f and Q-V loops
Frequency
Tie-Line flows
Generator
Output

## Slide 8
Files
Activities
Raw Data
RAWD
.RAW
Saved Cases
SAVE CASE
.SAV
.CNV
Response Files (Commands)
IDEV
.IDV
Dynamics Raw Data
DYRE
.DYR
Dynamics Cases
SNAP
.SNP
Dynamics Plot Files (channel output)
STRT (also ESTR,GSTR)
.OUT
Slider Diagram Files
One-line diagrams
.SLD
PYTHON
Command line input & program automation
.PY
Dynamic Simulation – Common file types
Sequence Data
SAV
.SEQ

## Slide 9
Documentation…Model Library

## Slide 10
Documentation…Model Library…Examples(1)

## Slide 11
Documentation…Model Library…Examples(2)

## Slide 12
DYR file contents

## Slide 13
Dynamics Data – Spreadsheet View

## Slide 14
Dynamics Data – Spreadsheet View…(2)

## Slide 15
Data Checking…(1)
To ensure model parameters are within acceptable limits
Necessary for stable simulation model
Dynamics -> Model List -> Models and Data (DOCU) -> Data checking mode

## Slide 16
Data Checking…(2)

## Slide 17: This page is intentionally kept blank

## Slide 18: SAARC Workshop on Load/Power Flow Studies using PSS/E for Efficient National & Cross Border Interconnected Power Systems in South Asia
Session II : Dynamic Simulation Activities
Day-3
Thimphu, Bhutan
18th to 20th July 2018

## Slide 19
Logic Flow for Simulation…(1)
Start with a solved PSS/E power flow case (RAW / SAV formats)
  Ideally solution in 1-2 iterations
Prepare power flow case for dynamic simulation:
Convert loads and generators
Power flow → Convert Loads and Generators
CONL and CONG
Optimally order network matrix
Power flow → Solution → Order Network…
ORDR
Factorize network admittance matrix (Y-bus matrix)
Power flow → Solution → Factorize admittance matrix FACT
Solve converted case
Power flow → Solution → Solution for switching studies
TYSL

## Slide 20
Logic Flow for Simulation…(2)
Note with Load Conversion activity:
  Using 100% constant P, Q is conservative approach (from Voltage stability point)
  Use Real power = 100% Constant I, Reactive power = 100% Constant Z
Load dynamics raw data and simulate:
Load Dynamics raw data (*.dyr format)
File -> Open -> DYRE
Define Channels for recording simulation output
Dynamics -> Define simulation output / Define simulation output by subsystem
CHAN / CHSB
Initialize dynamics case
Dynamics -> Simulation -> Perform Simulation -> Initialize
STRT
Run dynamics case in time steps
Dynamics -> Simulation -> Perform Simulation ->
RUN

## Slide 21
Models summary

## Slide 22
STRT/RUN
How often to write channel data to progress window
How often to write channel data to channel output file
How often to plot selected channels on CRT
Print
Write
Plot

## Slide 23
Simulation Options

## Slide 24
Initialisation OK

## Slide 25: Initial Conditions suspect
Executing activity STRT
GENROU AT BUS GENROU AT BUS IEEET1 AT BUS IEEET1 AT BUS SCRX AT BUS TGOV1 AT BUS
101 MACHINE 1 : X'' =0.12000 IM(ZSORCE) =0.30000
102 MACHINE 1 : X'' =0.12000 IM(ZSORCE) =0.30000
MACHINE 1
MACHINE 1
201 MACHINE 1
206 MACHINE 1
INITIALIZED OUT OF LIMITS INITIALIZED OUT OF LIMITS INITIALIZED OUT OF LIMITS INITIALIZED OUT OF LIMITS
INITIAL CONDITION LOAD FLOW USED 1 ITERATIONS
--------------------------MACHINE INITIAL CONDITIONS--------------------------- X------ BUS -----X ID ETERM EFD POWER VARS P.F. ANGLE ID IQ
101 | NUC-A | 21.6 | 1 | 1.0200 | 2.3091 | 750.00 | 151.11 | 0.9803 | 62.50 | 0.7010 | 0.4507
102 | NUC-B | 21.6 | 1 | 1.0200 | 2.3091 | 750.00 | 151.11 | 0.9803 | 62.50 | 0.7010 | 0.4507
201 HYDRO 500 1 1.014912.0906 600.00 400.00 0.8320 30.58 0.8186 0.5388 |  |  |  |  |  |  |  |  |  |  | 
206 | URBGEN | 18.0 | 1 | 0.9717 | 2.4921 | 800.00 | 600.00 | 0.8000 | 26.85 | 0.9358 | 0.4283
3001 | MINE | 230 | 1 | 1.0500 | 1.6566 | 248.88 | 187.25 | 0.7991 | 13.60 | 0.2291 | 0.1884
3008 | CATDOG | 230 | 1 | 0.9517 | 2.8515 | 100.00 | 80.00 | 0.7809 | 22.06 | 0.9583 | 0.3913
INITIAL | CONDITIONS | SUSPECT: |  |  |  |  | 
I | DSTATE(I) | STATE(I) | MODEL | STATE | BUS | X--- NAME ---X | ID
13 | -1.4181 | 2.0860 | GENSAL | K | 201 | HYDRO 500.00 | 1
22 | -0.24039E-01 | 0.0000 | GENROU | K+4 | 206 | URBGEN 18.000 | 1
38 | -2.0250 | 2.3091 | IEEET1 | K+2 | 101 | NUC-A 21.600 | 1
42 | -2.0250 | 2.3091 | IEEET1 | K+2 | 102 | NUC-B 21.600 | 1
63 | -0.24039 | 4.8636 | TGOV1 | K+1 | 206 | URBGEN 18.000 | 1

## Slide 26
Save simulation data
To Save dynamics simulation data:
  Save Converted power flow case as *.cnv file
  Save Dynamics model data as *.dyr (RAW file) or *.snp (Snapshot file)
  Save Channels as *.idv file
  Simulation is automatically stored in *.out / *.outx file

## Slide 27
Creating a Disturbance and Clearing it

## Slide 28
Viewing Simulation results

## Slide 29
References
PSSE 34.4 Documentation
Power System Stability and Control, P.Kundur
Ewart, D.N.; DeMello, F.P., "A Digital Computer Program for the Automatic Determination of Dynamic Stability Limits," Power Apparatus and Systems, IEEE Transactions on , vol.PAS-86, no.7, pp.867,875, July 1967

## Slide 30: Thank You !!